## Technical Information
Technical Information
SunSpec Modbus Interface
SunSpec_Modbus-TI-en-13 ¦ Version 1.3
Information on this Document
This document is a supplement to the technical description "SunSpec® Modbus® interface". It contains device-specific SunSpec Modbus registers for SMA inverters with Speedwire interface. The individual sheets are named by the corresponding inverter type and firmware version. In each case a sheet contains the supported SunSpec Modbus registers of a device with short descriptions. The tables in each case contain several grey markers that identify the beginnings of the SunSpec models supported by this inverter. For additional information, please see the technical description referenced under "Additional Information". When directly connected to a TCP/IP network, the SunSpec Modbus registers of a device are accessible under the Unit ID = 126.
Additional Information
Additional information is available at www.SMA-Solar.com
Document title, Document type
SunSpec® Modbus® interface, technical description
Legal Provisions
The information contained in this document is the property of SMA Solar Technology AG. Any publication, whether in whole or in part, requires prior written approval by SMA Solar Technology AG. Internal reproduction used solely for the purpose of product evaluation or other proper use is allowed and does not require prior approval.
Trademarks
All trademarks are recognized, even if not explicitly identified as such. A lack of identification does not mean that a product or symbol is not trademarked.
Modbus® is a registered trademark of Schneider Electric and is licensed by the Modbus Organization, Inc.
SunSpec® is a registered trademark of SunSpec Alliance, Inc.
SMA SOLAR TECHNOLOGY AG
Sonnenallee 1
34266 Niestetal
Deutschland
Tel. +49 561 9522-0
Fax +49 561 9522-100
www.SMA.de
E-Mail: info@SMA.de
© 2016 SMA Solar Technology AG. All rights reserved.

## SMA Device Types
SMA Device Types
Device Type IDs | Type Designation | Explanation
9067 | STP 10000TL-10 | This sheet breaks down SMA device type IDs to SMA type designations.
9068 | STP 12000TL-10 | The device type IDs in each case are provided by Modbus register address 40037 with the designation "Model ID".
9069 | STP 15000TL-10
9070 | STP 17000TL-10
9074 | SB 3000TL-21
9075 | SB 4000TL-21
9076 | SB 5000TL-21
9165 | SB 3600TL-21
9162 | SB 3500TL-JP-22
9164 | SB 4500TL-JP-22
9181 | STP 20000TLEE-10
9182 | STP 15000TLEE-10
9184 | SB 2500TLST-21
9185 | SB 3000TLST-21
9194 | STP 12000TL-US-10
9195 | STP 15000TL-US-10
9196 | STP 20000TL-US-10
9197 | STP 24000TL-US-10
9310 | STP 30000TL-US-10
9198 | SB 3000TL-US-22
9199 | SB 3800TL-US-22
9200 | SB 4000TL-US-22
9201 | SB 5000TL-US-22
9274 | SB 6000TL-US-22
9275 | SB 7000TL-US-22
9293 | SB 7700TL-US-22
9223 | Sunny Island 6.0H
9224 | Sunny Island 8.0H
9278 | Sunny Island 3.0M
9279 | Sunny Island 4.4M
9225 | SB 5000SE-10
9226 | SB 3600SE-10
9222 | STP 10000TLEE-JP-10
9271 | STP 20000TLEE-JP-11
9272 | STP 10000TLEE-JP-11
9284 | STP 20000TL-30
9285 | STP 25000TL-30
9301 | SB 1.5-1VL-40
9302 | SB 2.5-1VL-40
9304 | SB 5.0-1SP-US-40
9305 | SB 6.0-1SP-US-40
9311 | STP 25000TL-JP-30

## STP nn000TL-10, PKG 2.65
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Tripower with "Speedwire data module"
Sunny Tripower: STP 10000TL-10, STP 12000TL-10, STP 15000TL-10, STP 17000TL-10
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.65.02.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 2 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RW
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40349 | WMaxLimPct | Set power output to specified level | uint16 | RW
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 | uint16 | RW
40359 | VArWMaxPct | Reactive power in percent of WMax | int16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RW
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval: 0 | uint16 | RW
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40476 | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband | uint16 | RW
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RW
40481 | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced | int16 | RW
40482 | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced | uint16 | RW
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40485 | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40497 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail: 0 | uint16 | RW
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40672 | ID | MPPT 3: Input ID | uint16 | RO
40673 |  |  | uint16
40692 | ID | MPPT 4: Input ID | uint16 | RO
40712 | ID | MPPT 5: Input ID | uint16 | RO
40732 | ID | MPPT 6: Input ID | uint16 | RO

## SB nn00TL-21, PKG 2.60
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Boy with "Speedwire data module"
Sunny Boy: SB 3000TL-21, SB 3600TL-21, SB 4000TL-21, SB 5000TL-21
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.60.05.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 101 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 1 2 3 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 0 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## SB n000TL-JP-22, PKG 2.62
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: C31400204883 | uint32 | RO | Sunny Boy JP version with "Speedwire data module"
Sunny Boy: SB 3500TL-JP-22, SB 4500TL-JP-22
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.62.30.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 1 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## STP nn000TLEE-10, PKG 2.50
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Tripower Economic Excellence with "Speedwire data module"
Sunny Tripower: STP 15000TLEE-10, STP 20000TLEE-10
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.50.87.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 | uint16 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40476 | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband: 0 1 | uint16 | RW
40479 | ModEna | Activate dynamic reactive current model: 0 1 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40481 | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced | int16 | RW
40482 | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced | uint16 | RW
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40485 | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 0 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## SB nn00TLST-21, PKG 2.60
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Boy with "Speedwire data module"
Sunny Boy: SB 2500TLST-21, SB 3000TLST-21
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.60.05.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 101 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 1 2 3 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 0 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## STP nn000TL-US-10, PKG 2.81
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Tripower US version with "Speedwire data module"
Sunny Tripower: STP 12000TL-US-10, STP 15000TL-US-10, STP 20000TL-US-10, STP 24000TL-US-10 and STP 30000TL-US-10
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.81.00.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 2 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40348 | Conn | Enumerated valued. Connection control | uint16 | RW
40349 | WMaxLimPct | Set power output to specified level | uint16 | RW
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 | uint16 | RW
40354 | OutPFSet | Set power factor to specific value - cosine of angle | int16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 | uint16 | RW
40359 | VArWMaxPct | Reactive power in percent of WMax | int16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40476 | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband | uint16 | RW
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40481 | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced | int16 | RW
40482 | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced | uint16 | RW
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40485 | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## SB n000TL-US-22, PKG 2.62
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Boy US version with "Speedwire data module"
Sunny Boy: SB 3000TL-US-22, SB 3800TL-US-22, SB 4000TL-US-22 and SB 5000TL-US-22
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Sunny Boy: SB 6000TL-US-22, SB 7000TL-US-22 and SB 7700TL-US-22
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Speedwire data module: SWDM-10
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO | Starting with software package: 2.62.30.R
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 102 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40193 | PPVphAB | Phase Voltage AB | uint16 | RO
40194 | PPVphBC | Phase Voltage BC | uint16 | RO
40195 | PPVphCA | Phase Voltage CA | uint16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 0 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## SI 6.0-8.0H-11, PKG 3.1
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO | Sunny Island with "Speedwire data module Sunny Island"
40045 | Vr | Manufacturer specific value (16 chars): | string8 | RO | Sunny Island: SI 6.0H-11 and SI 8.0H-11
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO | Speedwire data module Sunny Island: SWDMSI-NR10
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO | Starting with software package: 3.100
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40200 | W | AC Power | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40372 | WChaMax | Setpoint for maximum active charging power. Reference value for WChaGra, WDisChaGra | uint16 | RW
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40378 | ChaState | Currently available energy as a percent of the capacity rating | uint16 | RO
40380 | InBatV | Internal battery voltage | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW

## SI 3.0-4.4M-11, PKG 3.2
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO | Sunny Island with "Speedwire data module Sunny Island"
40045 | Vr | Manufacturer specific value (16 chars): | string8 | RO | Sunny Island: SI 3.0M-11 and SI 4.4M-11
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO | Speedwire data module Sunny Island: SWDMSI-NR10
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO | Starting with software package: 3.200
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40200 | W | AC Power | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40372 | WChaMax | Setpoint for maximum active charging power. Reference value for WChaGra, WDisChaGra | uint16 | RW
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40378 | ChaState | Currently available energy as a percent of the capacity rating | uint16 | RO
40380 | InBatV | Internal battery voltage | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW

## SB 3600-5000SE-10, PKG 2.05
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Boy Smart Energy
Sunny Boy Smart Energy: SB 3600SE-10 and SB 5000SE-10
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Starting with software package: 2.05.02.R
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 | uint16 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40257 | WHRtg | Nominal energy rating of storage device | uint16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40261 | MaxChaRte | Maximum rate of energy transfer into the storage device | uint16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40263 | MaxDisChaRte | Maximum rate of energy transfer out of the storage device | uint16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40372 | WChaMax | Setpoint for maximum active charging power. Reference value for WChaGra, WDisChaGra | uint16 | RW
40378 | ChaState | Currently available energy as a percent of the capacity rating | uint16 | RO
40380 | InBatV | Internal battery voltage | uint16 | RO
40381 | ChaSt | Charge status of storage device. Enumerated value | uint16 | RO
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval: 0 | uint16 | RW
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40484 | HysBlkZnV | Hysteresis voltage used with BlkZnV | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40497 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail: 0 | uint16 | RW
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO
40672 | ID | MPPT 3: Input ID | uint16 | RO
40681 | DCA | MPPT 3: DC Current | uint16 | RO
40682 | DCV | MPPT 3: DC Voltage | uint16 | RO
40683 | DCW | MPPT 3: DC Power | uint16 | RO
40692 | ID | MPPT 4: Input ID | uint16 | RO
40701 | DCA | MPPT 4: DC Current | uint16 | RO
40702 | DCV | MPPT 4: DC Voltage | uint16 | RO
40703 | DCW | MPPT 4: DC Power | uint16 | RO
40712 | ID | MPPT 5: Input ID | uint16 | RO
40721 | DCA | MPPT 5: DC Current | uint16 | RO
40722 | DCV | MPPT 5: DC Voltage | uint16 | RO
40723 | DCW | MPPT 5: DC Power | uint16 | RO
40732 | ID | MPPT 6: Input ID | uint16 | RO
40741 | DCA | MPPT 6: DC Current | uint16 | RO
40742 | DCV | MPPT 6: DC Voltage | uint16 | RO
40743 | DCW | MPPT 6: DC Power | uint16 | RO

## STP nn000TLEE-JP10_11, PKG 2.63
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Tripower Economic Excellence with "Speedwire data module"
Sunny Tripower JP: STP 10000TLEE-JP-10, STP 10000TLEE-JP-11, STP 20000TLEE-JP-11
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.63.01.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40193 | PPVphAB | Phase Voltage AB | uint16 | RO
40194 | PPVphBC | Phase Voltage BC | uint16 | RO
40195 | PPVphCA | Phase Voltage CA | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 1 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40476 | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband: 0 1 | uint16 | RW
40479 | ModEna | Activate dynamic reactive current model: 0 1 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40481 | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced | int16 | RW
40482 | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced | uint16 | RW
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40485 | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## STP nn000TL-30, PKG 2.80
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Tripower with "Speedwire data module"
Sunny Tripower: STP 20000TL-30, STP 25000TL-30
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Speedwire data module: SWDM-10
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO | Starting with software package: 2.80.06.R
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3: 0 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40301 | StorConn | Storage inverter present/available status. Enumerated value: 0 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40476 | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband: 0 1 | uint16 | RW
40479 | ModEna | Activate dynamic reactive current model: 0 1 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40481 | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced | int16 | RW
40482 | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced | uint16 | RW
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40485 | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 0 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## SB nn-1VL-40, PKG 2.03
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Boy
Sunny Boy: SB 1.5-1VL-40 and SB 2.5-1VL-40
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Starting with software package: 2.03.02.R
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40192 | A_SF |  | int16 | RO
40193 | PPVphAB | Phase Voltage AB | uint16 | RO
40194 | PPVphBC | Phase Voltage BC | uint16 | RO
40195 | PPVphCA | Phase Voltage CA | uint16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40219 | TmpCab | Cabinet Temperature | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40250 | ARtg | Maximum RMS AC current level capability of the inverter | uint16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval: 0 | uint16 | RW
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 | uint16 | RW
40497 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail: 0 | uint16 | RW
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO
40672 | ID | MPPT 3: Input ID | uint16 | RO
40681 | DCA | MPPT 3: DC Current | uint16 | RO
40682 | DCV | MPPT 3: DC Voltage | uint16 | RO
40683 | DCW | MPPT 3: DC Power | uint16 | RO
40692 | ID | MPPT 4: Input ID | uint16 | RO
40701 | DCA | MPPT 4: DC Current | uint16 | RO
40702 | DCV | MPPT 4: DC Voltage | uint16 | RO
40703 | DCW | MPPT 4: DC Power | uint16 | RO
40712 | ID | MPPT 5: Input ID | uint16 | RO
40732 | ID | MPPT 6: Input ID | uint16 | RO

## STP nn000TL-JP-30, PKG 1.00
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Tripower with "Speedwire data module" Sunny Tripower JP: STP 25000TL-JP-30 Speedwire data module: SWDM-10
Starting with software package: 1.00.20.R
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40189 | AphA | Phase A Current | uint16 | RO
40190 | AphB | Phase B Current | uint16 | RO
40191 | AphC | Phase C Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40193 | PPVphAB | Phase Voltage AB | uint16 | RO
40194 | PPVphBC | Phase Voltage BC | uint16 | RO
40195 | PPVphCA | Phase Voltage CA | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40246 | VArRtgQ2 | Continuous VAR capability of the inverter in quadrant 2 | int16 | RO
40247 | VArRtgQ3 | Continuous VAR capability of the inverter in quadrant 3 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40253 | PFRtgQ2 | Minimum power factor capability of the inverter in quadrant 2 | int16 | RO
40254 | PFRtgQ3 | Minimum power factor capability of the inverter in quadrant 3 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 | uint16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 | uint16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40375 | StorCtl_Mod | Activate hold/discharge/charge storage control mode. Bitfield value: 0 | uint16 | RW
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval | uint16 | RO
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40476 | ArGraMod | Indicates if gradients trend toward zero at the edges of the deadband or trend toward zero at the center of the deadband | uint16 | RW
40479 | ModEna | Activate dynamic reactive current model: 0 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40481 | DbVMin | The lower delta voltage limit for which negative voltage deviations less than this value no dynamic vars are produced | int16 | RW
40482 | DbVMax | The upper delta voltage limit for which positive voltage deviations less than this value no dynamic current produced | uint16 | RW
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40485 | BlkZnTmms | Block zone time the time before which reactive current support remains active regardless of how low the voltage drops | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 | uint16 | RW
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RO
40503 | W1 | Point 1 Watts | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail | uint16 | RO
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO

## SB nn-1SP-US-40, PKG 2.01
SunSpec Modbus Profile
Modbus register number | SunSpec-Name | Description / Number code(s) | Type | Access | Supported hardware and firmware:
40001 | SID | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map: 1400204883 | uint32 | RO | Sunny Boy
Sunny Boy: SB 5.0-1SP-US-40 and SB 6.0-1SP-US-40
40003 | ID | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | uint16 | RO | Starting with software package: 2.01.17.R
40004 | L | Well-known # of 16 bit registers to follow : 66 | uint16 | RO
40005 | Mn | Well known value registered with SunSpec for compliance: SMA | string16 | RO
40021 | Md | Manufacturer specific value (32 chars): Solar Inverter | string16 | RO
40037 | Opt | Manufacturer specific value (16 chars): Model ID | string8 | RO
40045 | Vr | Manufacturer specific value (16 chars) | string8 | RO
40053 | SN | Manufacturer specific value (32 chars) | string16 | RO
40071 | ID | A well-known value 11. Uniquely identifies this as a SunSpec Ethernet Link Layer Model | uint16 | RO
40072 | L | Well-known # of 16 bit registers to follow : 13 | uint16 | RO
40073 | Spd | Interface speed in Mb/s: 0 10 100 | uint16 | RO
40074 | CfgSt | Bitmask values Interface flags: 0 1 3 | uint16 | RO
40075 | St | Enumerated value. State information for this interface: 0 1 2 | uint16 | RO
40076 | MAC | IEEE MAC address of this interface | uint64 | RO
40086 | ID | A well-known value 12. Uniquely identifies this as a SunSpec IPv4 Model | uint16 | RO
40087 | L | Well-known # of 16 bit registers to follow : 98 | uint16 | RO
40092 | CfgSt | Enumerated value. Configuration status | uint16 | RO
40093 | ChgSt | Bitmask value. A configuration change is pending | uint16 | RO
40094 | Cap | Bitmask value. Identify capable sources of configuration | uint16 | RO
40095 | Cfg | Enumerated value. Configuration method used: 0 1 | uint16 | RW
40096 | Ctl | Configure use of services | uint16 | RO
40097 | Addr | IPv4 numeric address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40105 | Msk | IPv4 numeric netmask as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40113 | Gw | IPv4 numeric gateway address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40121 | DNS1 | IPv4 numeric DNS address as a dotted string xxx.xxx.xxx.xxx | string8 | RW
40186 | ID | A well-known value 101,102,103. Uniquely identifies this as a SunSpec Inverter Model (101: 1-phase, 102: 2-phase, 103: 3-phase): 102 103 | uint16 | RO
40187 | L | Well-known # of 16 bit registers to follow : 50 | uint16 | RO
40188 | A | AC Current | uint16 | RO
40192 | A_SF |  | int16 | RO
40193 | PPVphAB | Phase Voltage AB | uint16 | RO
40194 | PPVphBC | Phase Voltage BC | uint16 | RO
40195 | PPVphCA | Phase Voltage CA | uint16 | RO
40196 | PhVphA | Phase Voltage AN | uint16 | RO
40197 | PhVphB | Phase Voltage BN | uint16 | RO
40198 | PhVphC | Phase Voltage CN | uint16 | RO
40199 | V_SF |  | int16 | RO
40200 | W | AC Power | int16 | RO
40201 | W_SF |  | int16 | RO
40202 | Hz | Line Frequency | uint16 | RO
40203 | Hz_SF |  | int16 | RO
40204 | VA | AC Apparent Power | int16 | RO
40205 | VA_SF |  | int16 | RO
40206 | VAr | AC Reactive Power | int16 | RO
40207 | VAr_SF |  | int16 | RO
40208 | PF | AC Power Factor | int16 | RO
40209 | PF_SF |  | int16 | RO
40210 | WH | AC Energy | acc32 | RO
40212 | WH_SF |  | int16 | RO
40218 | DCW_SF |  | int16 | RO
40219 | TmpCab | Cabinet Temperature | int16 | RO
40223 | Tmp_SF |  | int16 | RO
40224 | St | Enumerated value. Operating state: 1 2 3 4 5 6 7 8 | uint16 | RO
40226 | Evt1 | Bitmask value. Event fields: 0 1 2 16 32 64 128 256 512 1024 2048 4096 8192 16384 32768 | uint32 | RO
40238 | ID | A well-known value 120. Uniquely identifies this as a SunSpec Nameplate Model | uint16 | RO
40239 | L | Well-known # of 16 bit registers to follow : 26 | uint16 | RO
40240 | DERTyp | Type of DER device. Default value is 4 to indicate PV device: 4 | uint16 | RO
40241 | WRtg | Continuous power output capability of the inverter | uint16 | RO
40242 | WRtg_SF | Scale factor | int16 | RO
40243 | VARtg | Continuous Volt-Ampere capability of the inverter | uint16 | RO
40244 | VARtg_SF | Scale factor | int16 | RO
40245 | VArRtgQ1 | Continuous VAR capability of the inverter in quadrant 1 | int16 | RO
40248 | VArRtgQ4 | Continuous VAR capability of the inverter in quadrant 4 | int16 | RO
40249 | VArRtg_SF | Scale factor | int16 | RO
40250 | ARtg | Maximum RMS AC current level capability of the inverter | uint16 | RO
40251 | ARtg_SF | Scale factor | int16 | RO
40252 | PFRtgQ1 | Minimum power factor capability of the inverter in quadrant 1 | int16 | RO
40255 | PFRtgQ4 | Minimum power factor capability of the inverter in quadrant 4 | int16 | RO
40256 | PFRtg_SF | Scale factor | int16 | RO
40258 | WHRtg_SF | Scale factor | int16 | RO
40260 | AhrRtg_SF | Scale factor for amp-hour rating | int16 | RO
40262 | MaxChaRte_SF | Scale factor | int16 | RO
40264 | MaxDisChaRte_SF | Scale factor | int16 | RO
40266 | ID | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | uint16 | RO
40267 | L | Well-known # of 16 bit registers to follow : 30 | uint16 | RO
40268 | WMax | Setting for maximum power output. Default to WRtg | uint16 | RW
40269 | VRef | Voltage at the PCC | uint16 | RW
40270 | VRefOfs | Offset from PCC to inverter | int16 | RW
40273 | VAMax | Setpoint for maximum apparent power. Default to VARtg | uint16 | RW
40278 | WGra | Default ramp rate of change of active power due to command or internal action | uint16 | RW
40286 | ECPNomHz | Setpoint for nominal frequency at the ECP | uint16 | RW
40287 | ConnPh | Identity of connected phase for single phase inverters. A=1 B=2 C=3 | uint16 | RW
40288 | WMax_SF | Scale factor for real power | int16 | RO
40289 | VRef_SF | Scale factor for voltage at the PCC | int16 | RO
40290 | VRefOfs_SF | Scale factor for offset voltage | int16 | RO
40291 | VMinMax_SF | Scale factor for min/max voltages | int16 | RO
40292 | VAMax_SF | Scale factor for apparent power | int16 | RO
40293 | VArMax_SF | Scale factor for reactive power | int16 | RO
40294 | WGra_SF | Scale factor for default ramp rate | int16 | RO
40297 | ECPNomHz_SF | Scale factor for nominal frequency | int16 | RO
40298 | ID | A well-known value 122. Uniquely identifies this as a SunSpec Measurements_Status Model | uint16 | RO
40299 | L | Well-known # of 16 bit registers to follow : 44 | uint16 | RO
40300 | PVConn | PV inverter present/available status. Enumerated value: 1 3 5 | uint16 | RO
40302 | ECPConn | ECP connection status: disconnected=0 connected=1: 0 1 | uint16 | RO
40303 | ActWh | AC lifetime active (real) energy output | acc64 | RO
40342 | Ris | Isolation resistance | uint16 | RO
40343 | Ris_SF | Scale factor for isolation resistance | int16 | RO
40344 | ID | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | uint16 | RO
40345 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40348 | Conn | Enumerated valued. Connection control: 0 1 | uint16 | RW
40349 | WMaxLimPct | Set power output to specified level | uint16 | RW
40353 | WMaxLim_Ena | Enumerated valued. Throttle enable/disable control: 0 1 | uint16 | RW
40354 | OutPFSet | Set power factor to specific value - cosine of angle | int16 | RW
40358 | OutPFSet_Ena | Enumerated valued. Fixed power factor enable/disable control: 0 1 | uint16 | RW
40359 | VArWMaxPct | Reactive power in percent of WMax | int16 | RW
40365 | VArPct_Mod | Enumerated value. VAR percent limit mode | uint16 | RO
40366 | VArPct_Ena | Enumerated valued. Percent limit VAr enable/disable control: 0 1 | uint16 | RW
40367 | WMaxLimPct_SF | Scale factor for power output percent | int16 | RO
40368 | OutPFSet_SF | Scale factor for power factor | int16 | RO
40369 | VArPct_SF | Scale factor for reactive power percent | int16 | RO
40370 | ID | A well-known value 124. Uniquely identifies this as a SunSpec Storage Model | uint16 | RO
40371 | L | Well-known # of 16 bit registers to follow : 24 | uint16 | RO
40388 | WChaMax_SF | Scale factor for maximum charge | int16 | RO
40392 | ChaState_SF | Scale factor for available energy percent | int16 | RO
40394 | InBatV_SF | Scale factor for battery voltage | int16 | RO
40396 | ID | A well-known value 126. Uniquely identifies this as a SunSpec Static Volt-VAR Model | uint16 | RO
40397 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40398 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40399 | ModEna | Is Volt-VAR control active: 0 1 | uint16 | RW
40403 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40404 | NPt | Number of curve points supported (maximum of 20) | uint16 | RO
40405 | V_SF | Scale factor for percent VRef | int16 | RO
40406 | DeptRef_SF | scale factor for dependent variable | int16 | RO
40407 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40408 | ActPt | Number of active points in array | uint16 | RW
40409 | DeptRef | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval: 0 2 | uint16 | RW
40410 | V1 | Point 1 Volts | uint16 | RW
40411 | VAr1 | Point 1 VARs | int16 | RW
40412 | V2 | Point 2 Volts | uint16 | RW
40413 | VAr2 | Point 2 VARs | int16 | RW
40414 | V3 | Point 2 Volts | uint16 | RW
40415 | VAr3 | Point 3 VARs | int16 | RW
40416 | V4 | Point 4 Volts | uint16 | RW
40417 | VAr4 | Point 4 VARs | int16 | RW
40418 | V5 | Point 5 Volts | uint16 | RW
40419 | VAr5 | Point 5 VARs | int16 | RW
40420 | V6 | Point 6 Volts | uint16 | RW
40421 | VAr6 | Point 6 VARs | int16 | RW
40422 | V7 | Point 7 Volts | uint16 | RW
40423 | VAr7 | Point 7 VARs | int16 | RW
40424 | V8 | Point 8 Volts | uint16 | RW
40425 | VAr8 | Point 8 VARs | int16 | RW
40426 | V9 | Point 9 Volts | uint16 | RW
40427 | VAr9 | Point 9 VARs | int16 | RW
40428 | V10 | Point 10 Volts | uint16 | RW
40429 | VAr10 | Point 10 VARs | int16 | RW
40430 | V11 | Point 11 Volts | uint16 | RW
40431 | VAr11 | Point 11 VARs | int16 | RW
40432 | V12 | Point 12 Volts | uint16 | RW
40433 | VAr12 | Point 12 VARs | int16 | RW
40458 | RmpTms | The time of the PT1 in seconds (time to accomplish a change of 95%) | uint16 | RW
40459 | RmpDecTmm | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef | uint16 | RW
40460 | RmpIncTmm | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef | uint16 | RW
40461 | ReadOnly | Boolean flag indicates if curve is read-only or can be modified | uint16 | RO
40462 | ID | A well-known value 127. Uniquely identifies this as a SunSpec Freq-Watt Param Model | uint16 | RO
40463 | L | Well-known # of 16 bit registers to follow : 10 | uint16 | RO
40464 | WGra | The slope of the reduction in the maximum allowed watts output as a function of frequency | uint16 | RW
40465 | HzStr | The frequency deviation from nominal frequency (ECPNomHz) at which a snapshot of the instantaneous power output is taken to act as the CAPPED power level (PM) and above which reduction in power output occurs | int16 | RW
40466 | HzStop | The frequency deviation from nominal frequency (ECPNomHz) at which curtailed power output may return to normal and the cap on the power level value is removed | int16 | RW
40467 | HysEna | Enable hysterisis: 0 1 | uint16 | RW
40468 | ModEna | Is Parameterized Frequency-Watt control active: 0 1 | uint16 | RW
40469 | HzStopWGra | The maximum time-based rate of change at which power output returns to normal after having been capped by an over frequency event | uint16 | RW
40470 | WGra_SF | Scale factor for output gradient | int16 | RO
40471 | HzStrStop_SF | Scale factor for frequency deviations | int16 | RO
40472 | RmpIncDec_SF | Scale factor for increment and decrement ramps | int16 | RO
40474 | ID | A well-known value 128. Uniquely identifies this as a SunSpec Dynamic Reactive Current Model | uint16 | RO
40475 | L | Well-known # of 16 bit registers to follow : 14 | uint16 | RO
40479 | ModEna | Activate dynamic reactive current model: 0 1 | uint16 | RW
40480 | FilTms | The time window used to calculate the moving average voltage | uint16 | RO
40483 | BlkZnV | Block zone voltage which defines a lower voltage boundary below which no dynamic current is produced | uint16 | RW
40484 | HysBlkZnV | Hysteresis voltage used with BlkZnV | uint16 | RW
40487 | ArGra_SF | Scale factor for the gradients | int16 | RO
40488 | VRefPct_SF | Scale factor for the voltage zone and limit settings | int16 | RO
40490 | ID | A well-known value 131. Uniquely identifies this as a SunSpec Watt-PF Model | uint16 | RO
40491 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40492 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40493 | ModEna | Is watt-PF mode active: 0 1 | uint16 | RW
40497 | NCrv | Number of curves supported (recommend 4) | uint16 | RO
40498 | NPt | Max number of points in array | uint16 | RO
40499 | W_SF | Scale factor for percent WMax | int16 | RO
40500 | PF_SF | Scale factor for PF | int16 | RO
40502 | ActPt | Number of active points in array | uint16 | RW
40503 | W1 | Point 1 Watts | int16 | RW
40504 | PF1 | Point 1 PF in EEI notation | int16 | RW
40505 | W2 | Point 2 Watts | int16 | RW
40506 | PF2 | Point 2 PF in EEI notation | int16 | RW
40507 | W3 | Point 3 Watts | int16 | RW
40508 | PF3 | Point 3 PF in EEI notation | int16 | RW
40509 | W4 | Point 4 Watts | int16 | RW
40510 | PF4 | Point 4 PF in EEI notation | int16 | RW
40511 | W5 | Point 5 Watts | int16 | RW
40512 | PF5 | Point 5 PF in EEI notation | int16 | RW
40513 | W6 | Point 6 Watts | int16 | RW
40514 | PF6 | Point 6 PF in EEI notation | int16 | RW
40515 | W7 | Point 7 Watts | int16 | RW
40516 | PF7 | Point 7 PF in EEI notation | int16 | RW
40517 | W8 | Point 8 Watts | int16 | RW
40518 | PF8 | Point 8 PF in EEI notation | int16 | RW
40519 | W9 | Point 9 Watts | int16 | RW
40520 | PF9 | Point 9 PF in EEI notation | int16 | RW
40521 | W10 | Point 10 Watts | int16 | RW
40522 | PF10 | Point 10 PF in EEI notation | int16 | RW
40523 | W11 | Point 11 Watts | int16 | RW
40524 | PF11 | Point 11 PF in EEI notation | int16 | RW
40525 | W12 | Point 12 Watts | int16 | RW
40526 | PF12 | Point 12 PF in EEI notation | int16 | RW
40551 | RmpPT1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%) | uint16 | RW
40552 | RmpDecTmm | The maximum rate at which the power factor may be reduced in response to changes in the power value | uint16 | RW
40553 | RmpIncTmm | The maximum rate at which the power factor may be increased in response to changes in the power value | uint16 | RW
40554 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40556 | ID | A well-known value 132. Uniquely identifies this as a SunSpec Volt-Watt Model | uint16 | RO
40557 | L | Variable # of 16 bit registers to follow : 10+N*54 | uint16 | RO
40558 | ActCrv | Index of active curve. 0=no active curve: 0 1 | uint16 | RW
40559 | ModEna | Is Volt-Watt control active: 0 1 | uint16 | RW
40563 | NCrv | Number of curves supported (recommend min. 4) | uint16 | RO
40564 | NPt | Number of points in array (maximum 20) | uint16 | RO
40565 | V_SF | Scale factor for percent VRef | int16 | RO
40566 | DeptRef_SF | Scale Factor for % DeptRef | int16 | RO
40568 | ActPt | Number of active points in array | uint16 | RW
40569 | DeptRef | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail: 0 2 | uint16 | RW
40570 | V1 | Point 1 Volts | uint16 | RW
40571 | W1 | Point 1 Watts | int16 | RW
40572 | V2 | Point 2 Volts | uint16 | RW
40573 | W2 | Point 2 Watts | int16 | RW
40574 | V3 | Point 3 Volts | uint16 | RW
40575 | W3 | Point 3 Watts | int16 | RW
40576 | V4 | Point 4 Volts | uint16 | RW
40577 | W4 | Point 4 Watts | int16 | RW
40578 | V5 | Point 5 Volts | uint16 | RW
40579 | W5 | Point 5 Watts | int16 | RW
40580 | V6 | Point 6 Volts | uint16 | RW
40581 | W6 | Point 6 Watts | int16 | RW
40582 | V7 | Point 7 Volts | uint16 | RW
40583 | W7 | Point 7 Watts | int16 | RW
40584 | V8 | Point 8 Volts | uint16 | RW
40585 | W8 | Point 8 Watts | int16 | RW
40586 | V9 | Point 9 Volts | uint16 | RW
40587 | W9 | Point 9 Watts | int16 | RW
40588 | V10 | Point 10 Volts | uint16 | RW
40589 | W10 | Point 10 Watts | int16 | RW
40590 | V11 | Point 11 Volts | uint16 | RW
40591 | W11 | Point 11 Watts | int16 | RW
40592 | V12 | Point 12 Volts | uint16 | RW
40593 | W12 | Point 12 Watts | int16 | RW
40618 | RmpPt1Tms | The time of the PT1 in seconds (time to accomplish a change of 95%) | uint16 | RW
40619 | RmpDecTmm | The maximum rate at which the watt value may be reduced in response to changes in the voltage value | uint16 | RW
40620 | RmpIncTmm | The maximum rate at which the watt value may be increased in response to changes in the voltage value | uint16 | RW
40621 | ReadOnly | Enumerated value indicates if curve is read-only or can be modified | uint16 | RO
40622 | ID | A well-known value 160. Uniquely identifies this as a SunSpec Multiple MPPT Inverter Extension Model Model | uint16 | RO
40623 | L | Variable # of 16 bit registers to follow : 8+N*20 | uint16 | RO
40624 | DCA_SF | Current Scale Factor | int16 | RO
40625 | DCV_SF | Voltage Scale Factor | int16 | RO
40626 | DCW_SF | Power Scale Factor | int16 | RO
40630 | N | Number of Modules | uint16 | RO
40632 | ID | MPPT 1: Input ID | uint16 | RO
40641 | DCA | MPPT 1: DC Current | uint16 | RO
40642 | DCV | MPPT 1: DC Voltage | uint16 | RO
40643 | DCW | MPPT 1: DC Power | uint16 | RO
40652 | ID | MPPT 2: Input ID | uint16 | RO
40661 | DCA | MPPT 2: DC Current | uint16 | RO
40662 | DCV | MPPT 2: DC Voltage | uint16 | RO
40663 | DCW | MPPT 2: DC Power | uint16 | RO
40672 | ID | MPPT 3: Input ID | uint16 | RO
40681 | DCA | MPPT 3: DC Current | uint16 | RO
40682 | DCV | MPPT 3: DC Voltage | uint16 | RO
40683 | DCW | MPPT 3: DC Power | uint16 | RO
40692 | ID | MPPT 4: Input ID | uint16 | RO
40701 | DCA | MPPT 4: DC Current | uint16 | RO
40702 | DCV | MPPT 4: DC Voltage | uint16 | RO
40703 | DCW | MPPT 4: DC Power | uint16 | RO
40712 | ID | MPPT 5: Input ID | uint16 | RO
40721 | DCA | MPPT 5: DC Current | uint16 | RO
40722 | DCV | MPPT 5: DC Voltage | uint16 | RO
40723 | DCW | MPPT 5: DC Power | uint16 | RO
40732 | ID | MPPT 6: Input ID | uint16 | RO
40741 | DCA | MPPT 6: DC Current | uint16 | RO
40742 | DCV | MPPT 6: DC Voltage | uint16 | RO
40743 | DCW | MPPT 6: DC Power | uint16 | RO